## Sheet1
Measurement Procedure Chart of A Boiler Efficiency
Reference Standards：DL/T964-2005 and GB10184-88
Ying Xiaoyuan 3110103177, Wu Jiayang 3110103165, Wang Yihua 3110103119
Step 1
Input
Name |  |  |  |  | Symbol | Unit | Value
|  |  | 1 | Carbon Content(ARB) | Car | % | 89.86
|  | Elemental | 2 | Hydrogen Content(ARB) | Har | % | 3.29
|  | Analysis | 3 | Sulphur Content(ARB) | St,ar | % | 0.45
|  |  | 4 | Oxygen Content(ARB) | Oar | % | 5.26
|  |  | 5 | Nitrogen Content(ARB) | Nar | % | 1.14
Fuel(Coal) |  |  | 6 | Water Content(ARB) | Mt | % | 2.04
Characteristics |  |  | 7 | Water Content(ADB) | Mad | %
|  | Industrial | 8 | Ash Content(ARB) | Aar | % | 20.08
|  | Analysis | 9 | Volatile Matter Content(DAFB) | Vdaf | % | 5.97
|  |  | 10 | Net Calorific Power(ARB) | Qnet,ar | KJ/Kg | 26936.91
|  |  | 11 | Fuel Temperature | tr | ℃ | 23
|  |  | 12 | Total Moisture Content（石灰石全水分） | Mshst | % | 6
Desulfurizer（Limestone） |  |  | 13 | CaCO3 Content(ARB)（石灰石收到基碳酸钙含量） | CaCO3,ar | % | 85
Characteristics |  |  | 14 | CaCO3 Resolution Ratio（石灰石碳酸钙分解率） | βfj | % | 98
|  |  | 15 | Limestone Consumption（石灰石消耗量） | Bshs | Kg/h | 5500
Flue Gas Analysis |  |  | 16 | Oxygen Content | O2 | % | 4.6
|  |  | 17 | Specific Heat at Constant Pressure of O2 | Cp,O2 | KJ/(m3,k) | 1.3241
|  |  | 18 | Three Atomic Gases Content | RO2 | % | 13
|  |  | 19 | Specific Heat at Constant Pressure of CO2 | Cp,CO2 | KJ/(m3,k) | 1.7892
|  |  | 20 | Carbon Monoxide Content | CO | % | 0.005
|  |  | 21 | Specific Heat at Constant Pressure of CO | Cp,CO | KJ/(m3,k) | 1.3037
|  |  | 22 | Hydrogen Content | H2 | % | 0
|  |  | 23 | Nitrogen Content | N2 | % | 82.395
|  |  | 24 | Specific Heat at Constant Pressure of N2 | Cp,N2 | KJ/(m3,k) | 1.2972
|  |  | 25 | Methane Content | CH4 | % | 0
|  |  | 26 | Hydrocarbon Content | CmHn | % | 0
|  |  | 27 | Effluent Concentration of Sulfur Dioxide | SO2 | mg/m3 | 350
|  |  | 28 | Temperature | tdz | ℃ | 900
|  | Bottom | 29 | Specific Heat Capacity | Cdz | KJ/(Kg*K) | 0.8374
|  | Ash | 30 | Combustible Content | Ccdz | % | 1.77
|  |  | 31 | Ash Mass Content | αdz | % | 40
|  |  | 32 | Temperature | txhh | ℃ | 800
|  | Circulating | 33 | Specific Heat Capacity | Cxhh | KJ/(Kg*K) | 0.8374
|  | Ash | 34 | Combustible Content | Ccxhh | % | 5
Ash |  |  | 35 | Ash Mass Content | αxhh | % | 12
Characteristics |  | Fallout | 36 | Temperature | tcjh | ℃ | 200
|  |  | 37 | Specific Heat Capacity | Ccjh | KJ/(Kg*K) | 0.8374
|  |  | 38 | Combustible Content | Cccjh | % | 9.56
|  |  | 39 | Ash Mass Content | αcjh | % | 8
|  | Fly Ash | 40 | Specific Heat Capacity | Cfh | KJ/(Kg*K) | 0.8118
|  |  | 41 | Combustible Content | Ccfh | % | 13
|  |  | 42 | Ash Mass Content | αfh | % | 40
|  |  | 43 | Boiler Rated Evaporating Capacity | De | Kg/h | 400000
|  |  | 44 | Boiler Evaporating Capacity | D | Kg/h | 393000
|  |  | 45 | Atomizing Steam Content | Dwh | Kg/h | 0
|  |  | 46 | Enthalpy of Atomizing Steam in Inlet Parameter | hwh | KJ/Kg
|  |  | 47 | Enthalpy of Saturated Vapor at Datum Temperature | (hbq)0 | KJ/Kg
|  |  | 48 | Air Temperature（Ventilator Entrance） | t0 | ℃ | 20
|  |  | 49 | Air Absolute Humidity | dk |  | 0.012
|  |  | 50 | Specific Heat at Constant Pressure of Vapour（from t0 toθpy) | Cp,H2O | KJ/(Kg*K) | 1.5115
|  |  | 51 | Specific Heat at Constant Pressure of Air（based on Temperature at Ventilator Entrance) | (Cpk)0 | KJ/(Kg*K)
|  |  | 52 | Exhaust Gas Temperature | θpy | ℃ | 137
|  |  | 53 | Air Quantity of Entering Air Heater | VSF | m3/h
|  |  | 54 | Specific Heat at Constant Pressure of Air at Temperature of Air Heater Entrance | C"pk | KJ/(m3.K)
|  |  | 55 | Temperature of Air at Air Heater Entrance | t'k | ℃
Operation Parameter |  |  | 56 | Main Steam Flow | Dgq | Kg/h | 400000
of Boiler |  |  | 57 | Enthalpy of Main Steam | hgq | KJ/Kg | 3470.1
|  |  | 58 | Enthalpy of Feedwater | hgs | KJ/Kg | 858.98
|  |  | 59 | Vapour Flow at Reheater Entrance | D'zq | Kg/h | 350000
|  |  | 60 | Enthalpy of Vapour at Reheater Entrance | h'zq | KJ/Kg | 1200
|  |  | 61 | Enthalpy of Vapour at Reheater Exit | h"zq | KJ/Kg | 1690
|  |  | 62 | Desuperheater Water Flow of Reheater | Dzj | Kg/h | 0
|  |  | 63 | Desuperheater Water Enthalpy of Reheater | hzj | KJ/Kg | 700.98
|  |  | 64 | Extraction Mass of Saturated Steam | Dbq | Kg/h | 0
|  |  | 65 | Enthalpy of Saturation Water | hbs | KJ/Kg | 1706.5
|  |  | 66 | Enthalpy of Saturated Steam | hbq | KJ/Kg | 2532.62
|  |  | 67 | Effluent Flow | Dps | Kg/h | 0.01
|  |  | 68 | Area Correction Factor | fxz |  | 1.1
|  |  | 69 | Power Consumption of Main Auxiliary Engine | ∑Pfj | kW | 0
Step 2
Computational Process
Name |  |  |  |  | Symbol | Unit | Value
| Heat Loss of Exhaust Gas |  |  |  | Q2 | KJ/kg | 1832.954
| Heat of Dry Flue Gas |  |  |  | Qgy2 | KJ/kg | 1725.3199
| Sensible Heat of Vapour in Flue Gas |  |  |  | QH2O2 | KJ/kg | 107.6341
| Volume of Dry Flue Gas by Fuel Combustion |  |  |  | Vgy | m3/kg | 10.8238
| Specific Heat at Constant Pressure of Dry Flue Gas（from t0 toθpy) |  |  |  | Cp,gy | kJ/(m3.k) | 1.3624
| Volume of Dry Flue Gas by Fuel Combustion in Theory |  |  |  |  | m3/kg | 8.4363
| Excess Air Factor of Exhaust Gas in Fact |  |  |  | αpy |  | 1.2803
| Dry Flue Gas needed of Combustion in Theory |  |  |  |  | m3/kg | 8.5176
| Carbon Content(ARB) of Fuel in Fact |  |  |  | Crar | % | 87.6581
| Ca/S |  |  |  | Kglb |  | 6.5435
| Desulphurizing Rate |  |  |  | ηtl | % | 57.4678
Heat Loss | Last Assumed Desulphurizing Rate |  |  |  | η'tl，0 | % | 80
of Exhaust | Ash Content computed per Fuel |  |  |  | Ajs | % | 26.9348
Gas | Ratio of Average Carbon to Ash Content computed in Ash |  |  |  |  | % | 8.175
| Percentage of CaSO4 Amount after Desulfurization |  |  |  | ACaSO4 | % | 1.0991
| Percentage of Unreacted CaO Amount of Limestone per Fuel |  |  |  | ACaO | % | 4.5974
| Percentage of Undecomposed CaCO3 Amount of Limestone per Fuel |  |  |  | Awfj | % | 0.18404
| Percentage of Impurity Amount of Limestone per Fuel |  |  |  | Azz | % | 0.97431
| SO2 of Boiler Exhaust Gas Discharge Value Computed in Theory |  |  |  | SO20 | mg/m3 | 752.5431
| Actual SO2 Amount converted into that when αpy=1.4 in Dry Flue Gas |  |  |  | SO2,1.4 | mg/m3 | 320.0732
| Volume of Dry Flue Gas by Fuel Combustion（αpy=1.4） |  |  |  | Vgy,1.4 | m3/kg | 11.9594
| CaCO3 Content into Boiler per Fuel |  |  |  | bCaCO3 | % | 10.8257
| Volume of Vapour in Exhaust Gas |  |  |  | VH20 | m3/m3 | 0.60863
| Volume of Dry Flue Gas by Fuel Combustion in Theory（αpy=1.4） |  |  |  | (Vgy0)1.4 | m3/kg | 8.5524
| Dry Flue Gas needed of Combustion in Theory（αpy=1.4） |  |  |  | (Vgk0)1.4 | m3/kg | 8.5176
Heat Loss due to Unburned Combustible Gas |  |  |  |  | Q3 | KJ/kg | 6.8385
Heat Loss due to Unburned Carbon in Refuse |  |  |  |  | Q4 | KJ/kg | 742.0471
Heat Loss | Heat Loss under Rated Evaporating Capacity regardless of Area Correction |  |  |  | qe'5 | % | 0.60125
of Radiation | Heat Loss under Rated Evaporating Capacity |  |  |  | qe5 | % | 0.66137
Heat Loss due to Sensible Heat in Slag |  |  |  |  | Q6 | kJ/kg | 118.4014
Heat Loss of Limestone Desulfurization |  |  |  |  | Q7 | kJ/kg | 125.7251
Heat Input | Heat Input of Fuel |  |  |  | Qr | KJ/h | 1368734817.6444
| Net Calorific Power(ARB) of Fuel |  |  |  | QyDW | kJ/kg | 26936.91
| Physical Sensible Heat of Fuel |  |  |  | Qrx | kJ/kg | 2.9625
| External Heat |  |  |  | Qwl | kJ/h | 0
| Heat of Oil Fuel Atomizing Steam |  |  |  | Qwh | kJ/h | 0
| Heat due to Thawing |  |  |  | Qjd | kJ/kg | 6.834
| Equivalent Heat due to Power Consumption of Main Auxiliary Engine |  |  |  | ∑Qfj | kJ/h | 0
| Specific Heat of Fuel(Coal) |  |  |  | Cr | kJ/(kg.K) | 0.9875
| Specific Heat of Coal(MFB) |  |  |  | Cgr | kJ/(kg.K) | 0.92088
| Ash Content of Coal(MFB) |  |  |  | Ag | % | 20.4982
| Specific Heat of Ash |  |  |  | Ch | kJ/(kg.K) | 0.8104
| Specific Heat of Combustible Matter |  |  |  | Cr | kJ/(kg.K) | 0.94936
Heat Output |  |  |  |  | Q1 | kJ/h | 1215948008.4752
Step 3
Iterative Procedure
Name |  |  |  |  | Symbol | Unit | value
Assumed Desulphurizing Rate |  |  |  |  | ηtl，0 | % | 80
Last Iterated Result of Desulphurizing Rate |  |  |  |  | η’tl | % | 57.4678
Final Desulphurizing Rate by Computing |  |  |  |  | ηtl | % | 57.4678
Assumed Thermal Efficiency of Boiler |  |  |  |  | η0 | % | 90
Fuel Consumption |  |  |  |  | B | Kg/h | 50805.0438
Iterated Thermal Efficiency of Boiler |  |  |  |  | η' | % | 88.8408
Last Assumed Thermal Efficiency of Boiler |  |  |  |  | η'0 | % | 90
Final Thermal Efficiency of Boiler by Computing |  |  |  |  | η | % | 88.8374
Step 4
Computing Result
Input-Output Heat Method(Positive Balance Method)
Name |  |  |  |  | Symbol | Unit | Value
Heat Input |  |  |  |  | Qr | kJ/kg | 1368734817.6444
Heat Output |  |  |  |  | Q1 | kJ/kg | 1215948008.4752
Thermal Efficiency of Boiler |  |  |  |  | η | % | 88.8374
Heat Loss Method(Counter Balance Method)
Name |  |  |  |  | Symbol | Unit | Value
Percentage for Heat Loss of Exhaust Gas |  |  |  |  | q2 | % | 6.8036
Percentage for Heat Loss due to Unburned Combustible Gas |  |  |  |  | q3 | % | 0.025383
Percentage for Heat Loss due to Unburned Carbon in Refuse |  |  |  |  | q4 | % | 2.7543
Percentage for Heat Loss due to Radiation |  |  |  |  | q5 | % | 0.67315
Percentage for Heat Loss due to Sensible Heat in Slag |  |  |  |  | q6 | % | 0.43948
Percentage for Heat Loss of Limestone Desulfurization |  |  |  |  | q7 | % | 0.46667
Thermal Efficiency of Boiler |  |  |  |  | η | % | 88.8374
Notes:
1. Empirical formula in appendix for Heat Loss due to Radiation;
2. No heat absorption of cooling water in the slag cooler for heat loss due to sensible heat in slag and heat output.